# Table 9 of the CSE Phase II report as a CSV file

Extraction and checks of the performance data for 47 faecal sludge treatment plants in India

2026-09-29

Abstract

Table 9 of the 2023 Phase II report by the Centre for Science and Environment (CSE) gives the performance of 47 faecal sludge treatment plants (FSTPs) in India, grouped by technology. The report is only available as a PDF. We extracted Table 9 into a CSV file with an R script that reads the text of the PDF, and we describe the columns in a codebook. The CSV file has 47 rows and 10 columns, and every value is the same as in the printed table. All checks passed. They cover the number of rows, the value ranges, the codebook and a comparison with an independent transcription of the discharge BOD. The printed table has four problems, which we list but do not correct. Nalgonda has a missing value, the values for Amethi and Dhenkanal differ from other parts of the report, and the asterisk on Modinagar is not explained.

# 1. Introduction

Table 9 of the Phase II report by the Centre for Science and Environment (CSE) gives the performance of the 47 faecal sludge treatment plants (FSTPs) in the study (Narain et al. 2023). For each plant, the table gives the removal of chemical oxygen demand (COD), biochemical oxygen demand (BOD) and total Kjeldahl nitrogen (TKN). It also gives the pH, faecal coliforms, COD and BOD of the treated discharge water. Each value is the average of several sampling rounds.

The report is only available as a PDF, so the values cannot be used in an analysis without typing them again. We extracted Table 9 into a CSV file with a script, so that anyone can repeat the extraction and reuse the data.

# 2. Methods

## 2.1 Source

Table 9 is on pages 34 and 35 of the report, which is stored in this repository as data-raw/1689832445895.pdf. The table has one row per FSTP. The rows are grouped by technology, and each group starts with a header row.

## 2.2 Extraction

We extracted the table with the script data-raw/02-extract-fstp-performance.R, in the following steps:

- The text of pages 34 and 35 is read with pdftotext from the poppler library, which keeps the layout of the page.

- Each plant is assigned the technology of the group header above it.

- Each data row is found by its serial number and plant name.

- Each number is assigned to a column by its position on the page. The one empty cell in the table therefore stays empty, and the values after it do not shift.

- An error is raised if the number of rows, the rows per technology or the serial numbers differ from the printed table.

- The result is written to data-raw/table-09-fstp.csv.

Every value and plant name in the CSV file is the same as in the printed table, and we did not correct any value. The values are stored as numbers, so trailing zeros are dropped, e.g., 8.0 is stored as 8.

## 2.3 Columns

Table 1 describes the 10 columns of the CSV file. The same descriptions are in the codebook data-raw/codebook.csv, which also covers data-raw/bod-discharge.csv.

Table 1: Columns of the file table-09-fstp.csv, from the codebook. Variable; Type; Unit; Description. technology; character; Technology group of the FSTP. Short label for the group header row in Table 9: DEWATS, MBBR, Geotube, Mizuchi, Electrocoagulation-flotation or Packaged STP.. sno; integer; Serial number of the plant within its technology group, as printed in Table 9.. plant; character; FSTP location as printed in Table 9, including the asterisk on Modinagar.. cod_removal_pct; numeric; %; Removal of chemical oxygen demand (COD) from inlet to outlet. Average of the sampling rounds, as printed in Table 9.. bod_removal_pct; numeric; %; Removal of biochemical oxygen demand (BOD) from inlet to outlet. Average of the sampling rounds, as printed in Table 9. Empty for Nalgonda, where Table 9 has no value.. tkn_removal_pct; numeric; %; Removal of total Kjeldahl nitrogen (TKN) from inlet to outlet. Average of the sampling rounds, as printed in Table 9.. ph; numeric; pH of the treated discharge water. Average of the sampling rounds, as printed in Table 9.. faecal_coliform_mpn_100ml; numeric; MPN/100 mL; Faecal coliforms in the treated discharge water, as most probable number per 100 mL. Average of the sampling rounds, as printed in Table 9.. discharge_cod_mgl; numeric; mg/L; Chemical oxygen demand (COD) of the treated discharge water. Average of the sampling rounds, as printed in Table 9.. discharge_bod_mgl; numeric; mg/L; Biochemical oxygen demand (BOD) of the treated discharge water. Average of the sampling rounds, as printed in Table 9..

## 2.4 Checks

We checked the CSV file in the following ways:

- The number of rows, the rows per technology and the serial numbers agree with the printed table.

- The removal percentages are between 0 and 100, the pH values are between 0 and 14, and no value is negative.

- The codebook lists exactly the columns of the CSV file.

- The discharge BOD agrees with the file data-raw/bod-discharge.csv. For that file, we had typed the BOD values of Table 9 by hand and checked them against the PDF. The two files were made in different ways, so agreement between them is a check on both. For 10 plants, the names differ between the two files, e.g., “Kalibilod, Indore” in Table 9 and “Kalibillod” in the other file. We matched these plants with a lookup list.

These checks run every time the document is rendered. In addition, we compared every value in the CSV file once with the text of the PDF, row by row, and all 328 values matched.

# 3. Results

## 3.1 Extracted data

The CSV file has 47 rows and 10 columns (Table 2). Of the 329 value cells, 1 is empty, i.e., the BOD removal of Nalgonda, which Table 9 leaves blank. The full table is in the appendix (Table 4).

Table 2: Number of FSTPs per technology in the extracted table. Technology; Plants. DEWATS; 33. MBBR; 6. Geotube; 3. Mizuchi; 3. Electrocoagulation-flotation; 1. Packaged STP; 1. All; 47.

## 3.2 Checks

8 of the 8 checks passed (Table 3).

Table 3: Checks of the extracted table. The checks run every time the document is rendered. Check; Result. The CSV file has 47 rows; Passed. The rows per technology are 33, 6, 3, 3, 1 and 1; Passed. The serial numbers run from 1 to n within each technology; Passed. The removal percentages are between 0 and 100; Passed. The pH values are between 0 and 14; Passed. No value is negative; Passed. The codebook lists exactly the columns of the CSV file; Passed. The discharge BOD matches the independent transcription for all 47 plants; Passed.

## 3.3 Problems in the printed table

Table 9 has four problems. We kept the values as printed, so the same problems are in the CSV file:

- Nalgonda has no BOD removal value in Table 9 (page 35). Graph 5 (page 38) shows 97.2% for this plant.

- Amethi has 1.2% COD removal and 1.2% BOD removal, with 168 mg/L COD and 48.3 mg/L BOD in the discharge water (page 34). Table 5 of Annexure II (page 175) gives 107 mg/L COD and 30.1 mg/L BOD. Graph 4 (page 38) also gives 30.1 mg/L BOD, and Graph 5 (page 38) gives 29.0% BOD removal.

- Dhenkanal has 30.6 mg/L BOD in the discharge water (page 34). Table 3 of Annexure II (page 173) and Graph 32 (page 121) give 14.0 mg/L.

- Modinagar has an asterisk that Table 9 does not explain (page 35). Table 5 of the report (page 31) describes the plant as a hyper core (lamella) system.

# 4. Use notes

Anyone who reuses the CSV file should keep the following points in mind:

- Each value is an average over several sampling rounds, as printed in the report. The CSV file does not contain the single measurements.

- The values are not corrected. For Amethi and Dhenkanal, compare the values with the other parts of the report before using them.

- The plant names are the same as in Table 9 and can differ from other tables of the report, e.g., “Shandnagar” in Table 9 and “Shadnagar” in Table 1.

- To repeat the extraction, run Rscript data-raw/02-extract-fstp-performance.R from the root of the repository. The script needs pdftotext from the poppler library.

# References

Narain, Sunita, Vinod Vijayan, Sama Kalyana Chakravarthy, Megha Tyagi, Arvind Singh Senger, and Ashitha Gopinath. 2023. Evaluation of FSTPs and STP Co-Treatment Systems Across India: An Insight into Technology and Performance. Phase II study. Centre for Science and Environment.

# Appendix

Table 4: Table 9 of the report as extracted to table-09-fstp.csv. The empty cell is empty in the printed table. Technology; S No; Plant; COD removal (%); BOD removal (%); TKN removal (%); pH; Faecal coliform (MPN/100 mL); Discharge COD (mg/L); Discharge BOD (mg/L). DEWATS; 1; Siddipet; 97.9; 98.3; 95.4; 6.8; 6; 24.3; 6.3. DEWATS; 2; Sircilla; 58.9; 62.7; 46.1; 7.8; 549; 124.7; 24. DEWATS; 3; Thirumangalam; 67.5; 66.9; 95.4; 8.7; 14; 66.3; 16.3. DEWATS; 4; Thuraiyur; 82.5; 81.7; 98; 10.2; 30; 58.3; 15. DEWATS; 5; Vickramasingapuram; 83.8; 77.9; 83.8; 9.2; 251; 54.7; 14.7. DEWATS; 6; Shenkottai; 31.7; 32.6; 82.9; 8.9; 296; 172; 42.7. DEWATS; 7; Jhansi 12KLD; 59.4; 58; 55.9; 8.5; 2165; 75; 20. DEWATS; 8; Jhansi 6KLD; 48.3; 59; 72.6; 7.7; 16593; 144.4; 16.7. DEWATS; 9; Unnao; 89; 90.5; 82.8; 8; 69; 53.6; 8.4. DEWATS; 10; Chunar; 33.8; 48.3; 72.6; 7.4; 3820; 71; 20. DEWATS; 11; Amethi; 1.2; 1.2; 66.8; 8.7; 2400; 168; 48.3. DEWATS; 12; Phulera; 60.3; 70.5; 60.9; 8.5; 173; 148.2; 23.2. DEWATS; 13; Lalsot; 67.1; 71.3; 47.6; 8; 622; 121; 19.4. DEWATS; 14; Khandela; 61.7; 65.9; 53.6; 9.1; 35; 124.2; 22.4. DEWATS; 15; Balasore; 91.4; 73.5; 77.6; 7.5; 72; 146.3; 50. DEWATS; 16; Baripada; 79.1; 62.2; 49.9; 7.6; 5838; 367.3; 90. DEWATS; 17; Bhubaneswar; 83.7; 69.2; 64.2; 7.1; 314; 74.5; 25.7. DEWATS; 18; Dhenkanal; 51.1; 46.3; 80.7; 7.7; 61; 56; 30.6. DEWATS; 19; Berhampur; 80.3; 87.3; 82; 7.7; 300; 153.3; 27.6. DEWATS; 20; Angul; 49.8; 60.4; 68.5; 7.6; 16947; 162; 26.7. DEWATS; 21; Sambalpur; 49.6; 32.8; 89.8; 7.8; 9; 76.3; 14.1. DEWATS; 22; Rourkela; 68.9; 55.6; 89.8; 7.7; 5; 89.3; 18.2. DEWATS; 23; Asika; 95.2; 94.6; 93.1; 6.6; 30; 17; 6.1. DEWATS; 24; Bhadrak; 83.7; 83.2; 92.2; 8.1; 32; 105; 32.1. DEWATS; 25; Chodwar; 77.4; 76; 92.7; 8.3; 30; 43; 13.5. DEWATS; 26; Jagatsinghpur; 97.9; 98; 95.4; 7.3; 320; 24.7; 7.5. DEWATS; 27; Jatni; 73.3; 71.9; 76; 7; 32; 91.3; 28.5. DEWATS; 28; Khordha; 83.6; 82.7; 83.4; 6.6; 200; 65.7; 20.6. DEWATS; 29; Nimapada; 50; 48.6; 67.1; 8; 30; 31.5; 9. DEWATS; 30; Paralakhemundi; 95.5; 95; 95.2; 7.1; 33; 36; 10.5. DEWATS; 31; Patora, Raipur; 53.3; 58.5; 78.4; 8.4; 117; 89; 22. DEWATS; 32; Kumhari, Raipur; 59.7; 52.3; 75.2; 8.2; 2310; 68.7; 17. DEWATS; 33; Kalibilod, Indore; 60.9; 60.1; 62.3; 8; 4026; 119; 27.7. MBBR; 1; Kamareddy; 97.6; 96.9; 96.3; 7.3; 34; 40.33; 11. MBBR; 2; Nirmal; 73.8; 67.4; 82.8; 7.6; 235; 27; 7.5. MBBR; 3; Uppal; 54.8; 69.3; 94.5; 7.7; 55; 82; 14.33. MBBR; 4; Periyanaickenpalayam; 35.9; 41.7; 20.5; 8.6; 1330; 163.3; 37.3. MBBR; 5; Loni; 58.6; 60.9; 74.2; 7.9; 765; 231; 48. MBBR; 6; Modinagar*; 71.7; 71; 49.9; 8.2; 30; 44.5; 11. Geotube; 1; Boduppal; 91; 90.1; 91.3; 8.2; 14; 57.33; 13.33. Geotube; 2; Bongir; 78.3; 77.7; 96.2; 8.6; 29; 49; 11. Geotube; 3; Shandnagar; 95.8; 95.5; 92.9; 8.1; 46; 54.67; 13. Mizuchi; 1; Ojus, Jabalpur; 94.4; 93.7; 83.5; 7.105; 233; 19.5; 6.5. Mizuchi; 2; Elanza, Jabalpur; 94.7; 94.7; 87.3; 7.225; 14299; 38.5; 11.5. Mizuchi; 3; St.Alosius, Jabalpur; 80.6; 79.3; 72.2; 7.745; 133; 28; 8.6. Electrocoagulation-flotation; 1; Nalgonda; 92.6; 97.8; 8.2; 20; 41; 10.67. Packaged STP; 1; Warangal; 86.9; 85.1; 87.1; 8.3; 13; 46; 11.33.